# Fall River Police Department

City of Fall River

ADA Transition Plan

August 2019

200 Portland Street, Boston, MA 02114

www.IHCDesign.org • info@IHCDesign.org

617-695-1225 voice/tty

## Police Department

Year Built: 1997

## Background

The Fall River Police Department is located at 685 Pleasant Street. The building is a two (2) story building, with the upper floor that is not currently housing any public programs. Ground floor amenities include a main lobby, a community room used for public events and training sessions, and multi-user men’s and women’s toilet rooms. Additional amenities include rooms for processing detainees, and a visiting area. The Police Department also has a detention center in the north end of the building; there are 20 male holding cells included one mobility accessible cell and 6 female holding cells – there are no mobility accessible cell in the women’s area.

There is one (1) main entrance overlooking Pleasant Street, which also functions as an emergency exit. Three (3) additional emergency exits are provided in the secure detainee areas; all of which exit to the west-side staff parking area. Vertical circulation to the non-public area is provided by stairs and an elevator.

The parking lot is located to the east of the main entrance facing Pleasant Street. It has 19 spaces – two (2) are accessible.

## Key Accessibility Issues

### Exterior Access Routes

Accessibility issues include excessive running slope at the route from the gated emergency exits to the parking area.

### Emergency Exits

Accessibility issues include lack of tactile egress signs and lack of the International Symbol of Accessibility located on the illuminated exit signs at the emergency exits. Additionally, the gated emergency exit doors have thresholds that are higher than the maximum allowed.

### Detention Center

- The women’s area lacks an accessible mobility cell.

- The shower seat in the mobility cell in the men’s area is higher than the maximum allowed.

- The counter at the visiting area is higher than the maximum allowed and lacks a clear floor space positioned for a forward approach due to the fixed seat.

Note: Where a telephone is provided as a method to facilitate voice communication, a telephone equipped with volume control must be provided.

### Community Room

Accessibility issues include lack of an assistive listening system in the community room.

Note: Where a sound system, microphone and/or speaker are integral to the use of the space an assistive listening system (ALS) must be provided.

### Toilet Rooms

Accessibility issues include lack of insulated pipes at the lavatory (women’s toilet room located near the main lobby), doors with malfunctioning self-closing hinges and rear grab bars shorter than the minimum length required (men’s and women’s toilet rooms located near the community room). Other accessibility issues in the men’s toilet room near the community room include a flush control not located in the open/transfer side, toilet centerline greater than the maximum allowed and the urinal lacks a clear floor space. Additional issues include paper towel dispensers mounted higher than the maximum allowed (men’s and women’s toilet rooms located near the community room).

### Additional Accessibility Issues

- Lack of a drinking fountain for standing users.

- Walk-off mats are not securely attached.

- Lack of a compliant van accessible signs at the van accessible parking spaces.

## Order of Magnitude Cost Estimates

- Emergency exit renovations: $2,354

- Provide an assistive listening system in the community room: $1,821

- *Detention Area:

  - Provide compliant toilet/lavatory combo and compliant shower seat (detention cells): $15,208

  - Provide an accessible visiting area: $890

- Renovate toilet room: $6,130

- Provide a drinking fountain for a standing user: $3,021

- Miscellaneous corrective actions (parking, exterior access routes, egress signs, etc.): $2,308

Total: $31,732

*Cost to provide an accessible cell in the women’s detention area is not provided.

## Best Practice & Universal Design

Best practice and inclusive design recommendations include elements that are not required in the standards but may create enhanced experiences for all users.

- IHCD recommends providing a curb ramp on the opposite side of the main entrance crosswalk with detectable warnings.